## Slide 1
ADAPTIVE PREDICTIVE PREHEAT CONTROL · MOBILE & TEMPORARY STRUCTURES
✕
TEAM FENNERS × LB ENERGY GMBH
⟨ Add team member names here ⟩
Building of the Future — Intelligent Control of Mobile Structures
LB Energy GmbH × TUM Hackathon · June 2026

## Slide 2
THE CHALLENGE
Knowing the optimal moment to heat — made dynamic
OnQ Never Early · Never Late
Team Fenners × LB Energy GmbH
1
For each booking, find the latest moment preheat must start so the room hits 21 °C exactly when people arrive — no earlier (waste), no later (cold).
At LB Energy it's harder: many building types — tents, halls, insulated containers — each with different walls, air-trapping and thermal mass.
And they're temporary — up and down on varying timeframes — so there is no recorded history for any specific structure. Every deployment is a cold start.
Thin tent
very low insulation · tiny mass
τ ≈ minutes
Prefab container
medium insulation & mass
τ ≈ 1–4 h
Lecture hall
high insulation · large mass
τ ≈ 2–12 h
REAL DATA · TUM campus, 30 Mar 2026
The current system preheated a fixed 2 h 25 min ahead — the room was still 2.2 °C too cold at event start, and did not reach 21 °C until ~9 hours later.

## Slide 3
WHAT WE'RE BUILDING · 1
A self-calibrating grey-box physics model
OnQ Never Early · Never Late
Team Fenners × LB Energy GmbH
2
Separate the universal physics from the building-specific numbers.
The thermal equation is the same for every building.
Only 3 parameters {β₁, β₂, β₃} differ — insulation, heating effectiveness, ambient gains.
They are fitted automatically from each building's own sensor telemetry.
Physics extrapolates by design — a tent-trained model would mis-predict a container; the same equation with different β works for both.
dT/dt = β₁·(T_supply−T_room) + β₂·(T_room−T_out) + β₃
τ = −1/β₂ is the building's insulation time constant
DATA IN → SELF-CALIBRATE → DECISION
IHL heat-pump sensors
room temp · outside temp · supply-air temp · compressor / power
External
weather forecast (Open-Meteo) · power-grid stress / carbon intensity · calendar bookings
⟶ fit β₁, β₂, β₃ ⟶ optimal preheat start time t*
Grid-aware: within the preheat window we shift heating toward cleaner, lower-stress grid hours — same comfort, lower CO₂ and peak load.
STATUS · DONE
Calibration + trajectory simulator built — 0.17 °C ramp fit; preheat lead time derived at ~4.1 h (cheap Mode-1 only).

## Slide 4
WHAT WE'RE BUILDING · 2
Three intelligent insights on top of the model
OnQ Never Early · Never Late
Team Fenners × LB Energy GmbH
3
💰
Cost / energy
Start the cheap hot-water coil early so the expensive electric boost never fires.
~71% less
preheat-window energy
DONE
🛠️
Fault detection
Watch the gap between predicted and measured temperature; sustained drift = a fault.
tomorrow
pipeline ready
BUILDING
🌱
Sustainability
Convert saved kWh to CO₂ avoided, plus grid-aware scheduling & what-if scenarios.
223 kg
CO₂ avoided / 7 mornings
DONE
THE SAVINGS MECHANISM WE FOUND IN THE DATA — TWO HEATING MODES
Mode 1 fan + hot-water coil · ~4.7 kW · cheap
Mode 2 electric boost · 53–73 kW · ~15× more expensive
We start Mode 1 ~4 h earlier and never trigger Mode 2 — using only setpoint timing, the one lever we actually have.

## Slide 5
STAKEHOLDERS
Who the insights are for — and how they touch them
OnQ Never Early · Never Late
Team Fenners × LB Energy GmbH
4
Stakeholder | Insight that matters | How they interact
Facility manager | Comfort guaranteed, no per-building setup | Calendar in → preheat auto-scheduled; fault alerts
LB Energy | One model scales to any new structure in ~3 days | Generalisation instead of per-site tuning
Operator / finance | € saved, peak-demand boost avoided | What-if slider: setpoint · unit count · season
Sustainability / ESG | kWh & CO₂ avoided, reportable | Seasonal savings summary + grid-aware timing
Occupants | A 21 °C room, on time | Invisible — they just aren't cold

## Slide 6
RESULTS SO FAR
Same day, same data — replayed through OnQ
OnQ Never Early · Never Late
Team Fenners × LB Energy GmbH
5
0 → 7
of 7 mornings on-time
(was 0/7)
~71%
less preheat-window energy
Mode-1 only, no boost
0.17 °C
heat-up ramp fit (RMSE)
physics matches reality
~4.1 h
calibrated preheat lead
vs blind 2 h 25 min
Room temperature on the 04:30 event morning
Chart: 
| 00:00 | 00:30 | 01:30 | 02:05 | 02:30 | 03:00 | 03:30 | 04:00 | 04:30
OnQ (our controller) | 16.8 | 17 | 18.2 | 18.9 | 19.4 | 19.9 | 20.2 | 20.45 | 20.6
Current system | 16.8 | 16.8 | 16.8 | 16.87 | 17.2 | 17.6 | 18.1 | 18.5 | 18.8
Comfort target 20.5 °C | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5 | 20.5
Honesty note: current-system figures are observed; our comfort figure is the controller's prediction; savings are electrical, preheat-window only. Cooling-window backtest is still in progress.

## Slide 7
DAY 3 · PLANNED
What we'll build tomorrow
OnQ Never Early · Never Late
Team Fenners × LB Energy GmbH
6
1
Cross-window generalisation test
Fit β on the heating window, validate on the cooling window — insulation β₂ shouldn't change seasonally.
2
Cooling-window precool controller
Symmetric to the heating one, to complete the currently-pending cooling backtest.
3
Anomaly / fault early-warning
CUSUM on the prediction residual; test on a synthetic fault.
4
ML residual corrector (LightGBM)
Learn what physics misses (solar, occupancy); disabled-safe so the RC model always stands alone.
5
Demo dashboard (Streamlit)
Trajectory plot, savings, and a what-if slider.
6
Uncertainty + safe-margin scheduling
Confidence interval on t*; fall back to a fixed offset if calibration fails.
Guaranteed demo: even if items 2–5 slip, the RC model alone tells the full story — 0.17 °C fit, ~4 h-early counterfactual, 0/7→7/7, ~71% energy.

## Slide 8
FOR LB ENERGY
Open questions to sharpen the next steps
OnQ Never Early · Never Late
Team Fenners × LB Energy GmbH
7
1
Building footprint (m²), wall construction and glazing ratio — to validate calibrated β / τ.
2
What drove the setpoint switch to 21 °C at 02:05 UTC when the exported config says 0 min preheat?
3
Is the 43 kW power spike a real peak event or a measurement artefact?
4
Rated COP / refrigerant type — to sharpen the energy-savings numbers.
5
In production, is each heat pump a separate zone, or one space_id per hall?